## Calculator Instructions (hidden)
Energy Savings Calculator - Pump and Fan VFD Retrofit
Introduction
This calculator is designed to provide savings estimates for VFD fan and pump installations. The tool can be used in conjunction with site specific spot measurements and logged data of with generic load profiles and estimated full load motor loading. This tool has three specific calculation pages: 1) VFD Fan Analysis - fan applications 2) VFD Pump Analysis - Pump applications where system flow will vary throughout the year 3) Throttle Valve Analysis - Pump applications where system flow will remain constant and a VFD is being used to replace a throttling valve (e.g., triple-duty valve)
Fan Analysis Instructions
Step 1 | Enter fan motor information (motor hp and efficiency from motor nameplate or other documented source)
Step 2 | Estimate motor load factor, or use default load factor (80%).
Step 3 | Determine fan motor full load kW - the analysis will be based on a calculated value determined from Step 1, or the user may input full load kW based on field measurements:
If Full Load (100% flow) spot Power measurements have been taken enter the value in cell F8
If Full Load (100% flow) spot Amperage measurements are available, estimate full load kW using calculation method in cells C46:F46 and standard power factor table. Enter estimated kW calculated in cell B46 into cell F8
Step 4 | Enter the fan's annual hours of operation
Step 5 | Select existing and proposed control systems
The control type selection determines which standard part load performance curve will be used in the calculations. All part load curves were taken from the Bonneville Power Administration published documents
The curves were developed from data obtained by measuring the operating characteristics of various pumps and from information provided in "Flow Control", a Westinghouse publication, Bulletin B-851, F/86/Rev-CMS 8121.
https://save-energy-now.org/EM/tools/Documents/pumps/VSD%20Calculator%20for%20Pumps%20Tip%20Sheet.pdf
Step 6 | Select annual load profile
If annual load profile is known from site metered data or site specific schedules select "custom or metered" in cell B25. Enter annual load profile in cells D29:D39
If annual load profile is not known, select a generic load profile in cell B25 which represents the expected annual load profile
Savings Calculation Method
The results of the analysis are presented in the table and graphs to the right of the input section. The savings values presented are calculated as follows:
Annual hours of operation (column M) for each of the pump load bins is determined by multiplying the load profile % by the total annual hours of operation
The existing (column N) and proposed (column Q) full load power percentage is taken from the fan load curves located on the "Fan Curves" worksheet
The existing (column O) and proposed (column R) pump power is determined by multiplying the full load pump power( cell F7 or F8) by the corresponding full load power percentage
The existing (column P) and proposed (column S) annual energy usage (kWh) is determined by multiplying the associated full load power by the total annual hours in that bin
The total annual energy savings is the sum of difference between the annual energy usage of the existing and proposed usage (cell P23 - cell S23)
Pump Analysis Instructions
Step 1 | Enter pump motor information (motor hp and efficiency from motor nameplate or other documented source)
Step 2 | Estimate motor load factor, or use default load factor (80%).
Step 3 | Determine pump motor full load kW - the analysis will be based on a calculated value determined from Step 1, or the user may input full load kW based on field measurements:
If Full Load (100% flow) spot Power measurements have been taken enter the value in cell F8
If Full Load (100% flow) spot Amperage measurements are available, estimate full load kW using calculation method in cells C46:F46 and standard power factor table. Enter estimated kW calculated in cell B46 into cell F8
Step 4 | Enter the pump's annual hours of operation
Step 5 | Select existing and proposed control systems
The control type selection determines which standard part load performance curve will be used in the calculations. All part load curves were taken from the Bonneville Power Administration published documents
The curves were developed from data obtained by measuring the operating characteristics of various pumps and from information provided in "Flow Control", a Westinghouse publication, Bulletin B-851, F/86/Rev-CMS 8121.
Step 6 | Select annual load profile
If annual load profile is known from site metered data or site specific schedules select "custom or metered" in cell B25. Enter annual load profile in cells D29:D39
If annual load profile is not known, select a generic load profile in cell B25 which best represents the expected annual load profile the pump will serve
Savings Calculation Method
The results of the analysis are presented in the table and graphs to the right of the input section. The savings values presented are calculated as follows:
Annual hours of operation (column M) for each of the pump load bins is determined by multiplying the load profile % by the total annual hours of operation
The existing (column N) and proposed (column Q) full load power percentage is taken from the fan load curves located on the "Fan Curves" worksheet
The existing (column O) and proposed (column R) pump power is determined by multiplying the full load pump power( cell F7 or F8) by the corresponding full load power percentage
The existing (column P) and proposed (column S) annual energy usage (kWh) is determined by multiplying the associated full load power by the total annual hours in that bin
The total annual energy savings is the sum of difference between the annual energy usage of the existing and proposed usage (cell P23 - cell S23)
Throttle Valve Instructions
Step 1 | Enter pump motor information (motor hp and efficiency from motor nameplate or other documented source)
Step 2 | Estimate motor load factor, or use default load factor (80%).
Step 3 | Determine pump motor power - the analysis will be based on a calculated value determined from Step 1, or the user may input motor power based on field measurements:
If Full Load (100% flow) spot Power measurements have been taken enter the value in cell F8
If Full Load (100% flow) spot Amperage measurements are available, estimate full load kW using calculation method in cells C46:F46 and standard power factor table. Enter estimated kW calculated in cell B46 into cell F8
If no full load spot measurements are available, estimate motor load factor in cell F6
Step 4 | Enter the pump's annual hours of operation
Step 5 | Determine existing system flow:
If the system flow is known from site metered data or spot measurements select "Known Existing Capacity" in cell E22 and enter the flow as a percentage of the full load GPM in cell F26
If only the existing valve position is known select "Known Valve Position" in cell E22 and enter the valve percent open position in cell F26
Savings Calculation Method
The results of the analysis are presented in the table to the right of the input section. The savings values presented are calculated as follows:
The existing system power is determined from the measured value, or calculated based on the percent load reduction caused by using a throttling devise
The throttling devise moves the system curve to the left and the pump's power is reduced (known as riding the pump curve)
| System % Flow |  | Calculated from either the value in cell F26 if "Know Existing Capacity" is selected or calculated from a standard throttle position curve contained on the "Throttling valve curves" worksheet if "Know valve position" is selected
| Existing System - Full Load Power |  | Calculated from throttle valve regression curve from "Pump Curves" worksheet and the system % flow
| Proposed System - Full Load Power |  | Calculated from VSD regression curve from "Pump Curves" worksheet and the system % flow
The total annual energy savings is the sum of difference between the annual energy usage of the existing and proposed usage (cell P12 - cell S12)

## SVP HVAC Pump VSD Savings Calc
HVAC Pump VSD Rebate Calculator - Silicon Valley Power
Submit a 1-page report for each size and type of variable speed drive proposed.
Instructions
1 | Enter the business customer name and address
2 | Enter an identifier for where the VSD is located
3 | Enter the VSD motor size (horsepower)
4 | Enter the quantity of VSDs
5 | Enter the pump motor annual operating hours
Note: You will be required to provide operating hour calculations and/or supporting documentation for operating hours exceeding 3,500 hours
6 | The energy savings and rebate amount are automatically calculated
7 | Select the Results Summary tab to see and print the estimate energy savings results.
8 | Submit this spreadsheet and a copy of the printed report with your SVP Customer Directed Rebate application.
| Date | 2017-06-19 13:09 | 42905.5482
Customer Name
Business Address
VSD location
VSD/Motor Size (HP)
Quantity
Annual Operating Hours
| Energy Savings (kWh/yr) | 0
| Rebate Amount | 0
Advanced Input - Load Profile
Use this section for determining energy savings from measured data
Instructions
1 | The calculator uses a typical HVAC pump load profile to estimate energy savings. The load profile defines the percent time a pump operates at different flows
2 | If you have measured or other credible sources of data substantiating your pump load profile, then a custom load profile may be entered in the below table.
Note: You will be required to provide the backup data for the custom profile entered
3 | Select "Yes" from the custom or metered data drop box.
4 | Enter the percent annual run time at the percent of full load.
5 | Note the sum of percent time must equal 100% for the savings results. A report showing "N/A" will not be accepted.
6 | The energy savings and rebate amount are automatically calculated
7 | Print the energy savings results (from the excel tool bar use file print function)
8 | Submit this spreadsheet and a copy of the printed report with your SVP Customer Directed Rebate application.
Use custom or metered data for the load profile?
No
| Percent Full Load | Percent Run Time
| Off | 0%
| 10% | 0%
| 20% | 0% |  | Example: A 1,000 gpm pump operates at 800 gpm for 2,000 of its 4,000 annual operating hours. Therefore a 50% run time (2,000/4,000 hours) is enter at 80% full load (800/1,000 gpm)
| 30% | 5%
| 40% | 5%
| 50% | 5%
| 60% | 10%
| 70% | 15%
| 80% | 50%
| 90% | 5%
| 100% | 5%
100%

## Results Summary
HVAC Pump VSD Rebate Calculator - Silicon Valley Power

## Fan Analysis (hidden)
HVAC Pump VSD Rebate Calculator - Silicon Valley Power
Fan Motor Information | [7 empty] | Savings Analysis Results
Quantity: |  |  |  | 1
Nameplate horsepower: |  |  |  | 40 | hp
Nameplate efficiency: |  |  |  | 93.04% | percent (from below reference table) |  |  | Annual energy savings, kWh |  | 31998.53
Default motor load factor: |  |  |  | 80% | percent |  |  | Percent savings |  | 49.84%
Calculated full load power: |  |  |  | 25.6823 | kW |  |  | EFLH of proposed system |  | 1245.9375
Or, Enter motor power, if measured: |  |  |  |  | kW (overrides calculated power; leave blank if unknown) | overrides calculated power - leave blank if unknown
Operating Parameters | [7 empty] | Part load performance |  | Existing system |  |  | Proposed system |  |  | Savings | Existing - Constant Volume
[8 empty] | % flow | Op hrs | Full load power | kW | kWh | Full load power | kW | kWh | kWh | Proposed - VSD
Hours per year fan operates: |  |  |  | 2500 | hrs/yr |  |  | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0
[8 empty] | 10% | 0 | 100% | 25.6823 | 0 | 4.75% | 1.2199 | 0 | 0
Fan Retrofit | [7 empty] | 20% | 0 | 100% | 25.6823 | 0 | 5.37% | 1.3791 | 0 | 0
[7 empty] | Look up table reference # | 30% | 0 | 100% | 25.6823 | 0 | 8% | 2.0546 | 0 | 0
Existing control type: |  |  | Constant Volume |  |  |  | 9 | 40% | 0 | 100% | 25.6823 | 0 | 12.89% | 3.3104 | 0 | 0
[8 empty] | 50% | 250 | 100% | 25.6823 | 6420.5729 | 20.27% | 5.2058 | 1301.4501 | 5119.1227
Proposed control type: |  |  | VSD |  |  |  | 2 | 60% | 500 | 100% | 25.6823 | 12841.1457 | 30.38% | 7.8023 | 3901.1401 | 8940.0056
[8 empty] | 70% | 750 | 100% | 25.6823 | 19261.7186 | 43.46% | 11.1615 | 8371.1429 | 10890.5757
[8 empty] | 80% | 500 | 100% | 25.6823 | 12841.1457 | 59.75% | 15.3452 | 7672.5846 | 5168.5611
[8 empty] | 90% | 375 | 100% | 25.6823 | 9630.8593 | 79.5% | 20.4174 | 7656.5331 | 1974.3262
[8 empty] | 100% | 125 | 100% | 25.6823 | 3210.2864 | 102.9% | 26.4348 | 3304.3478 | -94.0614
Load Curve Selection | [7 empty] | Total | 2500 |  |  | 64205.7285 |  |  | 32207.1986 | 31998.53
Load curve profile |  |  |  | Look up table reference #
HVAC fan |  |  |  | 2
HVAC fan |  | User Input
% flow | % time at Capacity | % time at Capacity |  | Analysis Profile
0% | 0% | 0% |  | 0%
10% | 0% | 0% |  | 0%
20% | 0% | 0% |  | 0%
30% | 0% | 5% |  | 0%
40% | 0% | 10% |  | 0%
50% | 10% | 20% |  | 10%
60% | 20% | 30% |  | 20%
70% | 30% | 20% |  | 30%
80% | 20% | 10% |  | 20%
90% | 15% | 5% |  | 15%
100% | 5% | 0% |  | 5%
Total | 100% | 100%
Estimating power (kW) from measured amps:
kW | amps | volts | ph | power factor
5.7366 | 8 | 460 | 3 | 0.9
Estimating power (kW) from rated full load amps:
kW | FLA | volts | ph | power factor | load factor
5.7366 | 10 | 460 | 3 | 0.9 | 0.8
Reference Table: Motor Efficiency |  |  |  | Rebate ($/kWh)
| Efficiency |  | Power Factor | 0.15
HP | Std | Prem. | Std | Prem.
0.001 | 50% | 55% | 50% | 55%
0.25 | 62.7% | 67.5% | 53.33% | 57.8%
0.33 | 66% | 68.8% | 62.42% | 64.16%
0.5 | 69% | 73.9% | 61.68% | 63.35%
0.75 | 76% | 78.5% | 66% | 74.55%
1 | 82.04% | 84.59% | 72.5% | 76.5%
1.5 | 83.67% | 85.83% | 72.9% | 77.2%
2 | 83.73% | 85.98% | 76.9% | 78.8%
3 | 86.12% | 88.54% | 78.1% | 80%
5 | 86.81% | 88.47% | 82.2% | 83.2%
7.5 | 88.16% | 90.08% | 83.1% | 83.4%
10 | 89.25% | 90.58% | 84% | 85.2%
15 | 90.02% | 91.37% | 84.7% | 84.7%
20 | 90.13% | 91.7% | 86% | 85.5%
25 | 91.73% | 92.57% | 85.9% | 85.8%
30 | 91.55% | 92.57% | 87.2% | 86.4%
40 | 91.86% | 93.04% | 86% | 85.6%
50 | 91.87% | 93.01% | 85.6% | 85.9%
60 | 92.8% | 93.48% | 87.3% | 85.8%
75 | 93.01% | 93.5% | 87.7% | 86.8%
100 | 93.19% | 93.77% | 87.8% | 86.3%
125 | 93.1% | 93.88% | 88.6% | 86.8%
150 | 93.47% | 94.24% | 88.8% | 86.9%
200 | 93.61% | 94.4% | 88.3% | 86.7%
300 | 95.3% | 95.8% | 90.4% | 86.8%
350 | 95.4% | 95.9% | 89.3% | 88.8%
400 | 95.3% | 95.6% | 89.4% | 86.9%
450 | 95% | 95% | 90% | 90%
500 | 95.2% | 95.2% | 90.5% | 90.5%
9999 | 95.2% | 95.2% | 90.5% | 90.5%

## Pump Analysis (hidden)
Pump Motor Information | [6 empty] | Savings Analysis Results
Quantity |  |  |  | 1
Nameplate horsepower: |  |  |  | 0.001 | hp
Nameplate efficiency: |  |  |  | 55% | percent |  | Annual energy savings, kWh |  | 0
Default motor load factor: |  |  |  | 80% | percent |  | Percent savings |  | #DIV/0!
Calculated full load power: |  |  |  | 0.0010861 | kW |  | EFLH of proposed system |  | 0
kW override (not used)
Existing - None-Constant Volume
Operating Parameters | [6 empty] | Part load performance |  | Existing system |  |  | Proposed system |  |  | Savings | Proposed - VSD
[7 empty] | % flow | Op hrs | Full load power | kW | kWh | Full load power | kW | kWh | kWh
Hours per year pump operates: |  |  |  | 0 | hrs/yr |  | 0% | 0 | 0% | 0 | 0 | 0% | 0 | 0 | 0
[7 empty] | 10% | 0 | 100% | 0.0010861 | 0 | 19.12% | 0.00020771 | 0 | 0
Pump Control Method Selection | [6 empty] | 20% | 0 | 100% | 0.0010861 | 0 | 14.32% | 0.00015558 | 0 | 0
[6 empty] | Look up table reference # | 30% | 0 | 100% | 0.0010861 | 0 | 13.05% | 0.00014173 | 0 | 0
Existing control type: |  |  | None-Constant Volume |  |  | 5 | 40% | 0 | 100% | 0.0010861 | 0 | 15.3% | 0.00016616 | 0 | 0
[7 empty] | 50% | 0 | 100% | 0.0010861 | 0 | 21.07% | 0.00022885 | 0 | 0
Proposed control type: |  |  | VSD |  |  | 2 | 60% | 0 | 100% | 0.0010861 | 0 | 30.37% | 0.00032983 | 0 | 0
[7 empty] | 70% | 0 | 100% | 0.0010861 | 0 | 43.19% | 0.00046907 | 0 | 0
[7 empty] | 80% | 0 | 100% | 0.0010861 | 0 | 59.53% | 0.00064659 | 0 | 0
[7 empty] | 90% | 0 | 100% | 0.0010861 | 0 | 79.4% | 0.00086239 | 0 | 0
[7 empty] | 100% | 0 | 100% | 0.0010861 | 0 | 102.8% | 0.0011165 | 0 | 0
Load Curve Selection | [6 empty] | Total | 0 |  |  | 0 |  |  | 0 | 0
Load curve profile |  |  |  | Look up table reference #
Medium Load |  |  |  | 3
Medium Load |  | User Input
% flow | % time at Capacity | % time at Capacity |  | Analysis Profile
0% | 0% | 0% |  | 0%
10% | 0% | 0% |  | 0%
20% | 0% | 0% |  | 0%
30% | 5% | 5% |  | 5%
40% | 10% | 5% |  | 10%
50% | 20% | 5% |  | 20%
60% | 30% | 10% |  | 30%
70% | 20% | 15% |  | 20%
80% | 10% | 50% |  | 10%
90% | 5% | 5% |  | 5%
100% | 0% | 5% |  | 0%
Total | 100% | 100%
Estimating power (kW) from measured amps:
kW | amps | volts | ph | power factor
5.7366 | 8 | 460 | 3 | 0.9
Estimating power (kW) from rated full load amps:
kW | FLA | volts | ph | power factor | load factor
5.7366 | 10 | 460 | 3 | 0.9 | 0.8
Motor Efficiency & Power Factor | [5 empty] | Rebate ($/kWh)
| Efficiency |  | Power Factor |  |  | 0.15
HP | Std | Prem. | Std | Prem.
0.001 | 50% | 55% | 50% | 55%
0.25 | 62.7% | 67.5% | 53.33% | 57.8%
0.33 | 66% | 68.8% | 62.42% | 64.16%
0.5 | 69% | 73.9% | 61.68% | 63.35%
0.75 | 76% | 78.5% | 66% | 74.55%
1 | 82.04% | 84.59% | 72.5% | 76.5%
1.5 | 83.67% | 85.83% | 72.9% | 77.2%
2 | 83.73% | 85.98% | 76.9% | 78.8%
3 | 86.12% | 88.54% | 78.1% | 80%
5 | 86.81% | 88.47% | 82.2% | 83.2%
7.5 | 88.16% | 90.08% | 83.1% | 83.4%
10 | 89.25% | 90.58% | 84% | 85.2%
15 | 90.02% | 91.37% | 84.7% | 84.7%
20 | 90.13% | 91.7% | 86% | 85.5%
25 | 91.73% | 92.57% | 85.9% | 85.8%
30 | 91.55% | 92.57% | 87.2% | 86.4%
40 | 91.86% | 93.04% | 86% | 85.6%
50 | 91.87% | 93.01% | 85.6% | 85.9%
60 | 92.8% | 93.48% | 87.3% | 85.8%
75 | 93.01% | 93.5% | 87.7% | 86.8%
100 | 93.19% | 93.77% | 87.8% | 86.3%
125 | 93.1% | 93.88% | 88.6% | 86.8%
150 | 93.47% | 94.24% | 88.8% | 86.9%
200 | 93.61% | 94.4% | 88.3% | 86.7%
300 | 95.3% | 95.8% | 90.4% | 86.8%
350 | 95.4% | 95.9% | 89.3% | 88.8%
400 | 95.3% | 95.6% | 89.4% | 86.9%
450 | 95% | 95% | 90% | 90%
500 | 95.2% | 95.2% | 90.5% | 90.5%
9999 | 95.2% | 95.2% | 90.5% | 90.5%

## Throttling Valve Analysis (hidden)
Pump Motor Information | [8 empty] | Savings Analysis Results
Enter nameplate horsepower: |  |  |  | 100 | hp
Enter nameplate efficiency: |  |  |  | 95% | percent |  |  |  | Annual energy savings (kWh) |  | 66960.748
Enter motor load factor: |  |  |  | 80% | percent (default 80%) |  |  |  | Percent savings |  | 27.84%
Calculated motor power: |  |  |  | 62.88 | kW
Or, Enter motor power, if measured: |  |  |  |  | kW (overrides calculated power; leave blank if unknown) | overrides calculated power - leave blank if unknown
Operating Parameters | [8 empty] | Part load performance |  | Existing system |  |  | Proposed system |  |  | Savings
[9 empty] | System % Flow | Op hrs | Full load power | kW | kWh | Full load power | kW | kWh | kWh
Enter hours per year pump operates: |  |  |  | 4000 | hrs/yr |  |  |  | 84.99% | 4000 | 95.63% | 60.1298 | 240519.119 | 69% | 43.3896 | 173558.3709 | 66960.748
[9 empty] | Total | 4000 |  |  | 240519.119 |  |  | 173558.3709 | 66960.748
Pump Control Method Selection
Look up table reference #
Select existing control type: |  |  | Throttle Valve |  |  |  |  | 6
Select proposed control type: |  |  | VSD |  |  |  |  | 2
Existing Flow Determination
Look up table reference #
Select flow calculation method: |  |  | Known Valve Position |  |  |  |  | 1
Estimated total flow
Enter existing valve position (percent open): |  |  |  | 50 | % |  |  | 84.99%
Enter existing flow capacity: |  |  |  | 80 | % |  | % of full load GPM
Estimating power (kW) from measured amps:
kW | amps | volts | ph | power factor
5.7366 | 8 | 460 | 3 | 0.9
Estimating power (kW) from rated full load amps:
kW | FLA | volts | ph | power factor | load factor
5.7366 | 10 | 460 | 3 | 0.9 | 0.8
Motor Efficiency & Power Factor
| Efficiency |  | Power Factor
HP | Std | Prem. | Std | Prem.
0.001 | 50% | 55% | 50% | 55%
0.25 | 62.7% | 67.5% | 53.33% | 57.8%
0.33 | 66% | 68.8% | 62.42% | 64.16%
0.5 | 69% | 73.9% | 61.68% | 63.35%
0.75 | 76% | 78.5% | 66% | 74.55%
1 | 82.04% | 84.59% | 72.5% | 76.5%
1.5 | 83.67% | 85.83% | 72.9% | 77.2%
2 | 83.73% | 85.98% | 76.9% | 78.8%
3 | 86.12% | 88.54% | 78.1% | 80%
5 | 86.81% | 88.47% | 82.2% | 83.2%
7.5 | 88.16% | 90.08% | 83.1% | 83.4%
10 | 89.25% | 90.58% | 84% | 85.2%
15 | 90.02% | 91.37% | 84.7% | 84.7%
20 | 90.13% | 91.7% | 86% | 85.5%
25 | 91.73% | 92.57% | 85.9% | 85.8%
30 | 91.55% | 92.57% | 87.2% | 86.4%
40 | 91.86% | 93.04% | 86% | 85.6%
50 | 91.87% | 93.01% | 85.6% | 85.9%
60 | 92.8% | 93.48% | 87.3% | 85.8%
75 | 93.01% | 93.5% | 87.7% | 86.8%
100 | 93.19% | 93.77% | 87.8% | 86.3%
125 | 93.1% | 93.88% | 88.6% | 86.8%
150 | 93.47% | 94.24% | 88.8% | 86.9%
200 | 93.61% | 94.4% | 88.3% | 86.7%
300 | 95.3% | 95.8% | 90.4% | 86.8%
350 | 95.4% | 95.9% | 89.3% | 88.8%
400 | 95.3% | 95.6% | 89.4% | 86.9%
450 | 95% | 95% | 90% | 90%
500 | 95.2% | 95.2% | 90.5% | 90.5%
9999 | 95.2% | 95.2% | 90.5% | 90.5%

## Lookup Tables (hidden)
Fan System Type |  | Pump System Types |  | Fan Curves |  | 3-Duty Flow Selection |  | Pump Curves
VSD | 2 | VSD | 2 | HVAC fan | 2 | Known Valve Position | 1 | Medium Load | 3
Eddy Current Drives | 3 | Eddy Current Drives | 3 | Medium Load | 3 | Known Existing Capacity | 2 | Low Load | 4
Inlet Guide Vane, FC Fans | 4 | Torque Converter | 4 | Low Load | 4 |  |  | Custom or Metered | 6
Inlet Guide Vane, BI & Airfoil Fans | 5 | None-Constant Volume | 5 | CO Garage Fan | 5
Inlet Damper Box | 6 | Throttle Valve | 6 | Custom or Metered | 6
Outlet Damper, FC Fans | 7
Outlet Damper, BI & Airfoil Fans | 8
Constant Volume | 9

## Pump Curves (hidden)
% Design Pump Power (kW)
| 2 | 3 | 4 | 5 | 6
% Capacity (GPM) | VSD | Eddy Current | Torque Converter | None-Constant Volume | Throttle Valve
0% | 27.4475 | 16.3968 | 13.5114 | 100 | 55.2124
10% | 19.1242 | 17.0391 | 18.1571 | 100 | 61.3924
20% | 14.3249 | 19.9754 | 24.9208 | 100 | 67.1924
30% | 13.0496 | 25.0257 | 33.3825 | 100 | 72.6124
40% | 15.2983 | 32.01 | 43.1222 | 100 | 77.6524
50% | 21.071 | 40.7483 | 53.7199 | 100 | 82.3124
60% | 30.3677 | 51.0606 | 64.7556 | 100 | 86.5924
70% | 43.1884 | 62.7669 | 75.8093 | 100 | 90.4924
80% | 59.5331 | 75.6872 | 86.461 | 100 | 94.0124
90% | 79.4018 | 89.6415 | 96.2907 | 100 | 97.1524
100% | 102.7945 | 104.4498 | 104.8784 | 100 | 99.9124

## Fan Curves (hidden)
% Design Fan Power (kW)
| 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
% Capacity (CFM) | VSD | Eddy Current | Inlet Guide Vane Control Forward Curve Fans | Inlet Guide Vane Control, BI & Airfoil Fans | Inlet Damper Box | Outlet Damper Control Forward Curve Fans | Outlet Damper Control, Radial Blade Backward Inclined & Airfoil Fans | Constant Volume
0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10% | 4.75 | 17 | 20.6428 | 52.6423 | 56.1011 | 22.2623 | 52.5601 | 100
20% | 5.37 | 20 | 21.5696 | 55.7547 | 59.8199 | 25.5956 | 53.2756 | 100
30% | 8 | 25 | 23.3204 | 57.4391 | 62.1947 | 30.4189 | 57.2351 | 100
40% | 12.89 | 32 | 26.4352 | 58.5355 | 64.0055 | 36.7323 | 63.5986 | 100
50% | 20.27 | 40.7 | 31.454 | 59.8839 | 66.0323 | 44.5356 | 71.5261 | 100
60% | 30.38 | 51.1 | 38.9168 | 62.3243 | 69.0551 | 53.8288 | 80.1776 | 100
70% | 43.46 | 62.8 | 49.3636 | 66.6967 | 73.8539 | 64.6121 | 88.7131 | 100
80% | 59.75 | 75.5 | 63.3344 | 73.8411 | 81.2087 | 76.8854 | 96.2926 | 100
90% | 79.5 | 89.6 | 81.3692 | 84.5975 | 91.8995 | 90.6487 | 102.0761 | 100
100% | 102.93 | 104.4 | 104.008 | 99.8059 | 106.7063 | 105.9021 | 105.2236 | 100

## VFD Load Curves (hidden)
| 2 | 3 | 4 | 5
% Capacity | HVAC fan | Medium Load | Low Load | CO Garage Sensor | Custom or Metered
0% | 0% | 0% | 5% | 60% | 0%
10% | 0% | 0% | 10% | 0% | 0%
20% | 0% | 0% | 10% | 0% | 0%
30% | 0% | 5% | 10% | 0% | 0%
40% | 0% | 10% | 20% | 0% | 0%
50% | 10% | 20% | 10% | 20% | 0%
60% | 20% | 30% | 10% | 10% | 0%
70% | 30% | 20% | 10% | 10% | 0%
80% | 20% | 10% | 10% | 0% | 0%
90% | 15% | 5% | 5% | 0% | 0%
100% | 5% | 0% | 0% | 0% | 0%
| 100% | 100% | 100% | 100%

## Throttling valve curves (hidden)
Typical valve/damper performance
% open | % flow
Typical valve
100 | 100
90 | 98
80 | 96
70 | 93
60 | 90
50 | 85
40 | 79
30 | 69
20 | 55
10 | 35
0 | 0
A | = design point, operating conditions with throttling valve partially closed
B | = operating conditions, throttling valve 100% open
C | = operating conditions, pump/fan speed reduced